Application Note 003

Guidelines for Scaling of Analog Inputs

Although any Analog Input can be scaled to any of the available scaling ranges it is more practical to follow some established guidelines for scaling ranges. A few of the Analog Inputs must follow mandatory scaling ranges for proper system operation. BAS makes recommendations for use of the other Analog Inputs to maintain consistency from one project to another. The following are the recommended scaling ranges:

Equipment Schedule 1, 2, 9

Input

Location	Range	Label	Use

AI1*	32.00-95.75	 F	Room Temperature

AI2	Var	 F	Zone SP Offset Pot

AI3	(-12.0)-115.5	 F	Outside Air Temperature

AI4 (1)	30.0-157.5	 F	Discharge Air Temperature

AI5	30.0-157.5	 F	Return Air Temperature

AI6	30.0-157.5	 F	Mixed Air Temperature

AI7	18.0-36.0	BTU/LBM	Outside Air Enthalpy

AI8	0-100	%	Aux Input

* Mandatory Inputs.

(1) Mandatory if used as a VariZone or VAV Server.

Equipment Schedule 3, 4, 10

Input

Location	Range	Label	Use

AI1*	32.00-95.75	 F	Room Temperature

AI2	Var	 F	Zone SP Offset Pot

AI3	30.0-157.5	 F	Return Air Temperature

AI4 (1)	30.0-157.5	 F	Discharge Air Temperature

* Mandatory Inputs.

(1) Mandatory if used as a VariZone or VAV Server.

Equipment Schedule 5-8, 11, 12

Input

Location	Range	Label	Use

AI1*	32.00-95.75	 F	Room Temperature

AI2 (1)	18.0-36.0	BTU/LBM	Return Air Enthalpy

AI3	(-12.0)-115.5	 F	Outside Air Temperature

AI4 (2)	30.0-157.5	 F	Discharge Air Temperature

AI5	30.0-157.5	 F	Return Air Temperature

AI6 (3)	30.0-157.5	 F	Mixed Air Temperature

AI7	18.0-36.0	BTU/LBM	Outside Air Enthalpy

AI8	Var	 F	Zone SP Offset Pot

* Mandatory Inputs.

(1) Mandatory if using an economizer.

(2) Mandatory if used as a VariZone or VAV Server.

(3) Mandatory if economizer is a modulating actuator controlled directly by RSC.

Equipment Schedule 23, 25, 27, 28

Input

Location	Range	Label	Use

AI1*	32.00-95.75	 F	Room Temperature

AI2 (1)	18.0-36.0	BTU/LBM	Return Air Enthalpy

AI3	(-12.0)-115.5	 F	Outside Air Temperature

AI4	30.0-157.5	 F	Discharge Air Temperature

AI5	30.0-157.5	 F	Return Air Temperature

AI6 (2)	30.0-157.5	 F	Mixed Air Temperature

AI7	18.0-36.0	BTU/LBM	Outside Air Enthalpy

AI8	Var	 F	Zone SP Offset Pot

* Mandatory Inputs.

(1) Mandatory if using an economizer.

(2) Mandatory if economizer is a modulating actuator controlled directly by RSC.

Equipment Schedule 13, 15, 17, 19, 20, 50, 52, 54, 56, 57

Input

Location	Range	Label	Use

AI1*	32.00-95.75	 F	Room Temperature

AI2 (1)	Var	CFM	Air Flow

AI3	(-12.0)-115.5	 F	Outside Air Temperature

AI4	30.0-157.5	 F	Discharge Air Temperature

AI5	30.0-157.5	 F	Return Air Temperature

AI6	30.0-157.5	 F	Mixed Air Temperature

AI7	18.0-36.0	BTU/LBM	Outside Air Enthalpy

AI8	Var	 F	Zone SP Offset Pot

* Mandatory Inputs.

(1) Mandatory if pressure independent control is used.

Equipment Schedule 14, 51

Input

Location	Range	Label	Use

AI1*	32.00-95.75	 F	Room Temperature

AI2 (1)	Var	CFM	Air Flow

or

AI2	Var	 F	Zone SP Offset Pot

* Mandatory Inputs.

(1) Mandatory if pressure independent control is used.

Equipment Schedule 16, 18, 53, 55, 60

Input

Location	Range	Label	Use

AI1*	32.00-95.75	 F	Room Temperature

AI2 (1)	(2)	CFM	Air Flow

AI3	Var	 F	Zone SP Offset Pot

AI4	30.0-157.5	 F	Supply Air Temperature

* Mandatory Inputs.

(1) Mandatory if pressure independent control is used.

Equipment Schedule 21, 22

Input

Location	Range	Label	Use

AI1*	32.00-95.75	 F	Room Temperature

AI2	30.0-157.5	 F	Discharge Air Temperature

or

AI2	Var	 F	Zone SP Offset Pot

* Mandatory Inputs.

Equipment Schedule 24, 26, 31

Input

Location	Range	Label	Use

AI1*	32.00-95.75	 F	Room Temperature

AI2 (1)	18.0-36.0	BTU/LBM	Return Air Enthalpy

AI3	Var	 F	Zone SP Offset Pot

AI4 (2)	30.0-157.5	 F	Mixed Air Temperature

* Mandatory Inputs.

(1) Mandatory if using an economizer.

(2) Mandatory if economizer is a modulating actuator controlled directly by RSC.

Equipment Schedule 29, 30

Input

Location	Range	Label	Use

AI1*	30.0-157.5	 F	Controlled Temperature

AI2	Var	 F	Zone SP Offset Pot

AI3	(-12.0)-115.5	 F	Outside Air Temperature

AI4	30.0-157.5	 F	Discharge Air Temperature

AI5	30.0-157.5	 F	Return Air Temperature

AI6	30.0-157.5	 F	Mixed Air Temperature

AI7	18.0-36.0	BTU/LBM	Outside Air Enthalpy

AI8	0-100	%	Aux Input

* Mandatory Inputs.

Equipment Schedule 32

Input

Location	Range	Label	Use

AI1*	30.0-157.5	 F	Water Loop Return Temperature

AI2	0-100	%	Aux Input

AI3	(-12.0)-115.5	 F	Outside Air Temperature

AI4	30.0-157.5	 F	Water Loop Supply Temperature

AI5	30.0-157.5	 F	Cooling Tower Outlet Temperature

AI6	0-255	 F	Boiler Outlet Temperature

AI7	18.0-36.0	BTU/LBM	Outside Air Enthalpy

AI8	0-100	%	Aux Input

* Mandatory Inputs.

Equipment Schedule 33

Input

Location	Range	Label	Use

AI1*	30.0-157.5	 F	Chilled Water Supply Temperature

AI2	0-100	%	Aux Input

AI3	(-12.0)-115.5	 F	Outside Air Temperature

AI4	30.0-157.5	 F	Chilled Water Return Temperature

AI5	30.0-157.5	 F	Water Loop Temperature

AI6	30.0-157.5	 F	Water Loop Temperature

AI7	18.0-36.0	BTU/LBM	Outside Air Enthalpy

AI8	0-100	%	Aux Input

* Mandatory Inputs.

Equipment Schedule 35, 36

Input

Location	Range	Label	Use

AI1*	0-255	 F	Hot Water Supply Temperature

AI2	0-100	%	Aux Input

AI3	(-12.0)-115.5	 F	Outside Air Temperature

AI4	0-255	 F	Hot Water Return Temperature

AI5	0-255	 F	Water Loop Temperature

AI6	0-255	 F	Water Loop Temperature

AI7	18.0-36.0	BTU/LBM	Outside Air Enthalpy

AI8	0-100	%	Aux Input

* Mandatory Inputs.

Equipment Schedule 40

Input

Location	Range	Label	Use

AI1*	30.0-157.5	 F	Discharge Air Temperature

AI2 (1)	18.0-36.0	BTU/LBM	Return Air Enthalpy

AI3	(-12.0)-115.5	 F	Outside Air Temperature

AI4 (2)	30.0-157.5	 F	Discharge Air Temperature

AI5	30.0-157.5	 F	Return Air Temperature

AI6 (3)	30.0-157.5	 F	Mixed Air Temperature

AI7	18.0-36.0	BTU/LBM	Outside Air Enthalpy

AI8	Var	 F	Zone SP Offset Pot

* Mandatory Inputs.

(1) Mandatory if using an economizer.

(2) Mandatory if used as a VariZone or VAV Server.

(3) Mandatory if economizer is a modulating actuator controlled directly by RSC.

Equipment Schedule 41, 42

Input

Location	Range	Label	Use

AI1*	Var	“ WC	Discharge Static Pressure

AI2	0-100	%	Aux Input

AI3	(-12.0)-115.5	 F	Outside Air Temperature

AI4	30.0-157.5	 F	Discharge Air Temperature

* Mandatory Inputs.