Application Note 007

Setup Calculations for Zone CFM Monitoring

Rev 1 RSC Only - Determination of Minimum Input Voltage

For sensors that use an input resistor, a minimum input voltage value must be determined in order to calculate an offset. Determine the minimum voltage at the AI terminal of the RSC as follows:

AI Min Volts = Esensmin - ((Esensmin * Rin)/(Rin + 46,625))

Esensmin = The minimum sensor output voltage as specified by the sensor manufacturer.

Rin = The value in ohms of the input resistor.

Determination of Offset

The Offset value must be input in the Actuators configuration at each Zone using a CFM sensor.

Rev 1 RSC

First determine the minimum voltage from the calculation above.

Offset = 255*AI MinVolts/3.8

Rev 3 RSC

Rev 3 RSCs use sensors that do not require an input resistor, and the minimum voltage is equal to the voltage as specified by the sensor manufacturer.

Offset = 255*AI MinVolts/5.0

AI MinVolts = The Vdc input to the RSC from the sensor corresponding to 0" wcd input.

Determination of BAS K

The BAS K value is input once in the VAV/VariZone Settings dialog. This value is used System-wide by all Zones.

BAS K = 10,000*SQR(Pmax/(255-Offset))

Pmax = The top end of the scale, in "wcd, of the pressure sensor being used.

Determination of CFM K for VAV Boxes

The CFM K value must be input in the Actuators configuration at each Zone using a CFM sensor.

Always use the CFM K as provided by the VAV box and/or air flow pick-up tube manufacturer. If that information is not available, then calculate a CFM K using the following:

CFM K = 4005 * Duct Area

Duct Area =  the cross sectional area of the duct where the velocity pressure sensor is 			located. The units of Duct Area are square feet.

For Round Ducts (Diam is in inches)

Duct Area = ( * (Diam/2)2) / 144

For Square or Rectangular Ducts (Length and Width are in inches)

Duct Area = (Length * Width) / 144